## Info
Template for IEC 60870-5-101/104 parameters IPC402x(exp) |  |  | Doc ID: IPC402x-LIST-01
These parameters exist for all IPC402x devices
These parameters exist only for IPC4020 and IPC4020exp3-6
These parameters exist only for IPC4022exp2-3 and IPC4020exp3-6
These parameters exist only for IPC4020exp4-6
These parameters exist only for Master option
These parameters exist only for Battery Supervision option
Please refer to the IPC402x Manual, available on www.protrol.se, for a detailed description on each parameter
The sheets are protected without password
Revision User Settings
Rev. No. | Comment | Date | Sign.
0 | First version | 20xx-xx-xx
1
2
IEC -101-104 Settings Template
Document: | IPC402x-LIST-1
Rev. no. | Comment | Date
00 | First version. | 2019-10-11 | MM/BF
01 | Enable static IP and trusted IP added. | 2019-11-01 | MM
02 | Factory settings revised in manual. | 2020-02-06 | MM
03 | Obj. Addr. divided. Remark added. | 2020-06-30 | MM
04 | Decimal address added. Protection added. | 2020-08-03 | MM
05 | Binary OUT: Object addresses updated for Det. 3 | 2020-10-23 | MM
06 | New columns added. | 2021-02-23 | MM
07 | PDCIO tabs added. IPC402x slave supervision added. | 2021-04-07 | MM | Gäller fr o m IPC firmware version 1-1.0.2
08 | PDCIO Analog IN: Object addresses adjusted. IPC402x Bin OUT: Logical outputs set to Direct Execute. Communication: Cyclic analog transmission set to 30 ms | 2021-09-13 | MM
09 | PDCIO Bin OUT: ACN object default pulse time set to 200 ms. IPC4020 Bin IN: Logical input 1 default type Double point. IPC4020 Bin OUT: Logical output 1 default type Double command. | 2022-01-20 | MM
10 | PDCIO Analog IN: PAI inputs changed to Normalized[0-100%] PDCIO Analog IN: PDCIO Unit temperature and PT100 input deadbands changed to 5% IPC402x BIN IN: SP changed to DP for RECL ON/OFF IPC402x BIN IN: SC changed to DC for RECL ON/OFF | 2022-02-02 | MM
11 | PDCIO Analog IN: PAI inputs changed to Float [SI] | 2022-04-06 | MM
12 | IPC402x Bin IN: Inputs 17-22 added. Detector 4-6 added. IPC402x Bin OUT: Outputs 9-13 added. Detector 4-6 added. IPC402x Analog IN: Detector 4-6 added. | 2022-09-30 | MM | Gäller fr o m IPC firmware version 1-2.0.0

## Communication
IPC402x Serial number:
Substation / Bay:
|  | Factory Default Settings | Custom Settings |  | Revision no | Comment
Ethernet | Enable static IP
Settings for | IP address | 192.168.0.31 | 192.168.0.31
unit: | Netmask | 255.255.255.0 | 255.255.255.0
| Gateway | 192.168.0.1 | 192.168.0.1
Trusted IP | IP address 1 | 192.168.0.101 | 192.168.0.101
addresses | Enable IP address 1
for IEC -104: | IP address 2 | 192.168.0.102 | 192.168.0.102
Enable IP address 2
| IP address 3 | 192.168.0.103 | 192.168.0.103
Enable IP address 3
| IP address 4 | 192.168.0.104 | 192.168.0.104
Enable IP address 4
| IP address 5 | 192.168.0.105 | 192.168.0.105
Enable IP address 5
IEC -101/104 | Common address (CA) | 1 | 1
Common | Use end of init (M_EI)
settings: | Slave interface | -104 slave | -104 slave
| Select timeout | 30 | 30
| Cyclic analog transmission | 30 | 30
| Master interface | No master | No master | *
-101 slave | Link address (LA) | 1 | 1
Protocol | Link address (LA) size | 1 | 1
settings: | Common address (CA) size | 2 | 2
| Object address (OA) size | 3 | 3
| Cause of transmission (COT) size | 2 | 2
Port settings: | Port type | 2-wire (RS-485) | 2-wire (RS-485)
| Baudrate | 9600 | 9600
| Response delay | 10 | 10
-104 slave | ADPU timeout (t1) | 15 | 15
Protocol | ACKN timeout (t2) | 10 | 10
settings: | TEST timeout (t3) | 30 | 30
| k unackn I format ASDU | 12 | 12
| W ackn I format ASDU | 8 | 8
| Command timetag timeout | 30 | 30
-101 master | Use master common address |  |  | *
Protocol
settings: | Link address (LA) size | 1 | 1 | *
| Common address (CA) size | 2 | 2 | *
| Object address (OA) size | 3 | 3 | *
| Cause of transmission (COT) size | 2 | 2 | *
Slave link | Slave 1 | 0 | 0
addresses: | Slave 2 | 0 | 0
| Slave 3 | 0 | 0
| Slave 4 | 0 | 0
| Slave 5 | 0 | 0
| Slave 6 | 0 | 0
| Slave 7 | 0 | 0
| Slave 8 | 0 | 0
| Slave 9 | 0 | 0
| Slave 10 | 0 | 0
Port settings: | Baudrate | 9600 | 9600 | *
* | Optional setting if the device is equipped with -101 master interface

## IPC402x Bin IN objects
[5 empty] | Factory Default Settings | [5 empty] | Custom Settings | [7 empty] | Circuit Diagram |  | Comissioning
| IPC402x: Binary inputs | [8 empty] | IEC IO Address | [5 empty] | IEC IO Address |  |  |  |  | Green |  | Revision
Internal input number | Products | Bay | Module input | Comment | Type | Blocked | Negative | Timetagged | Delay [ms] | Lower (16 bit) | Type | Blocked | Negative | Timetagged | Delay [ms] | Upper (8 bit) | Lower (16 bit) | Decimal | Page | Signal name | lined |  | no | Comment
0 | IPC402x | Common | Ack button | Object linked to the ACN button on the front panel | SP |  |  |  | 0 | 100 | SP |  |  |  | 0 |  | 100 | 100
1 | IPC402x | Common | Input 1 | Object linked to physical input 1 | SP |  |  |  | 0 | 101 | SP |  |  |  | 0 |  | 101 | 101
2 | IPC402x | Common | Input 2 | Object linked to physical input 2 | SP |  |  |  | 0 | 102 | SP |  |  |  | 0 |  | 102 | 102
3 | IPC402x | Common | Input 3 | Object linked to physical input 3 | SP |  |  |  | 0 | 103 | SP |  |  |  | 0 |  | 103 | 103
4 | IPC402x | Common | Input 4 | Object linked to physical input 4 | SP |  |  |  | 0 | 104 | SP |  |  |  | 0 |  | 104 | 104
5 | IPC402x | Common | Input 5 | Object linked to physical input 5 | SP |  |  |  | 0 | 105 | SP |  |  |  | 0 |  | 105 | 105
6 | IPC402x | Common | Input 6 | Object linked to physical input 6 | SP |  |  |  | 0 | 106 | SP |  |  |  | 0 |  | 106 | 106
7 | IPC402x | Common | Input 7 | Object linked to physical input 7 | SP |  |  |  | 0 | 107 | SP |  |  |  | 0 |  | 107 | 107
8 | IPC402x | Common | Input 8 | Object linked to physical input 8 | SP |  |  |  | 0 | 108 | SP |  |  |  | 0 |  | 108 | 108
9 | IPC4020/IPC4020exp | Common | Input 9 | Object linked to physical input 9 | SP |  |  |  | 0 | 109 | SP |  |  |  | 0 |  | 109 | 109
10 | IPC4020/IPC4020exp | Common | Input 10 | Object linked to physical input 10 | SP |  |  |  | 0 | 110 | SP |  |  |  | 0 |  | 110 | 110
11 | IPC4020/IPC4020exp | Common | Input 11 | Object linked to physical input 11 | SP |  |  |  | 0 | 111 | SP |  |  |  | 0 |  | 111 | 111
12 | IPC4020/IPC4020exp | Common | Input 12 | Object linked to physical input 12 | SP |  |  |  | 0 | 112 | SP |  |  |  | 0 |  | 112 | 112
13 | IPC4020/IPC4020exp | Common | Input 13 | Object linked to physical input 13 | SP |  |  |  | 0 | 113 | SP |  |  |  | 0 |  | 113 | 113
14 | IPC4020/IPC4020exp | Common | Input 14 | Object linked to physical input 14 | SP |  |  |  | 0 | 114 | SP |  |  |  | 0 |  | 114 | 114
15 | IPC4020/IPC4020exp | Common | Input 15 | Object linked to physical input 15 | SP |  |  |  | 0 | 115 | SP |  |  |  | 0 |  | 115 | 115
16 | IPC4020/IPC4020exp | Common | Input 16 | Object linked to physical input 16 | SP |  |  |  | 0 | 116 | SP |  |  |  | 0 |  | 116 | 116
17 | IPC402x | Common | IRF | Indication for internal error | SP |  |  |  | 0 | 117 | SP |  |  |  | 0 |  | 117 | 117
18 | IPC4020exp4-6 | Common | Input 17 | Object linked to physical input 17 | SP |  |  |  | 0 | 151 | SP |  |  |  | 0 |  | 151 | 151
| IPC4020exp4-6 | Common | Input 18 | Object linked to physical input 18 | SP |  |  |  | 0 | 152 | SP |  |  |  | 0 |  | 152 | 152
| IPC4020exp4-6 | Common | Input 19 | Object linked to physical input 19 | SP |  |  |  | 0 | 153 | SP |  |  |  | 0 |  | 153 | 153
| IPC4020exp4-6 | Common | Input 20 | Object linked to physical input 20 | SP |  |  |  | 0 | 154 | SP |  |  |  | 0 |  | 154 | 154
| IPC4020exp4-6 | Common | Input 21 | Object linked to physical input 21 | SP |  |  |  | 0 | 155 | SP |  |  |  | 0 |  | 155 | 155
| IPC4020exp4-6 | Common | Input 22 | Object linked to physical input 22 | SP |  |  |  | 0 | 156 | SP |  |  |  | 0 |  | 156 | 156
19 | IPC402x | 1 | OC Start | Overcurrent – START indication | SP |  |  |  | 0 | 120 | SP |  |  |  | 0 |  | 120 | 120
20 | IPC402x | 1 | OC1 Trip | Overcurrent – TRIP indication, level 1 | SP |  |  |  | 0 | 121 | SP |  |  |  | 0 |  | 121 | 121
21 | IPC402x | 1 | OC2 Trip | Overcurrent – TRIP indication, level 2 | SP |  |  |  | 0 | 122 | SP |  |  |  | 0 |  | 122 | 122
22 | IPC402x | 1 | EF Start | Earth fault – START indication | SP |  |  |  | 0 | 123 | SP |  |  |  | 0 |  | 123 | 123
23 | IPC402x | 1 | EF Trip | Earth fault – TRIP indication | SP |  |  |  | 0 | 124 | SP |  |  |  | 0 |  | 124 | 124
24 | IPC402x | 1 | EF Start (non-dir.) | Earth fault, non-directional – START indication | SP |  |  |  | 0 | 125 | SP |  |  |  | 0 |  | 125 | 125
25 | IPC402x | 1 | EF Trip (non-dir.) | Earth fault, non-directional – TRIP indication | SP |  |  |  | 0 | 126 | SP |  |  |  | 0 |  | 126 | 126
26 | IPC402x | 1 | Phase break | Indication for phase break | SP |  |  |  | 0 | 127 | SP |  |  |  | 0 |  | 127 | 127
27 | IPC402x | 1 | OC Trip Ind | Indication mirroring the LED OC Trip. | SP |  |  |  | 0 | 128 | SP |  |  |  | 0 |  | 128 | 128
28 | IPC402x | 1 | EF Trip Ind | Indication mirroring the LED EF Trip. | SP |  |  |  | 0 | 129 | SP |  |  |  | 0 |  | 129 | 129
29 | IPC402x | 1 | Logical input 1 | Option AR: RECL OFF/ON | DP |  |  |  | 0 | 0 | DP |  |  |  | 0 |  | 0 | 0 |  |  |  | *
30 | IPC402x | 1 | Logical input 2 | Reserved | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
31 | IPC402x | 1 | Logical input 3 | Reserved | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
32 | IPC4020exp | 2 | Reserved |  | SP | [5 empty] | SP
33 | IPC4020exp | 2 | Reserved |  | SP | [5 empty] | SP
34 | IPC4020exp | 2 | Reserved |  | SP | [5 empty] | SP
35 | IPC4020exp/IPC4022exp | 2 | OC Start | Overcurrent – START indication | SP |  |  |  | 0 | 220 | SP |  |  |  | 0 |  | 220 | 220
36 | IPC4020exp/IPC4022exp | 2 | OC1 Trip | Overcurrent – TRIP indication, level 1 | SP |  |  |  | 0 | 221 | SP |  |  |  | 0 |  | 221 | 221
37 | IPC4020exp/IPC4022exp | 2 | OC2 Trip | Overcurrent – TRIP indication, level 2 | SP |  |  |  | 0 | 222 | SP |  |  |  | 0 |  | 222 | 222
38 | IPC4020exp/IPC4022exp | 2 | EF Start | Earth fault – START indication | SP |  |  |  | 0 | 223 | SP |  |  |  | 0 |  | 223 | 223
39 | IPC4020exp/IPC4022exp | 2 | EF Trip | Earth fault – TRIP indication | SP |  |  |  | 0 | 224 | SP |  |  |  | 0 |  | 224 | 224
40 | IPC4020exp/IPC4022exp | 2 | EF Start (non-dir.) | Earth fault, non-directional – START indication | SP |  |  |  | 0 | 225 | SP |  |  |  | 0 |  | 225 | 225
41 | IPC4020exp/IPC4022exp | 2 | EF Trip (non-dir.) | Earth fault, non-directional – TRIP indication | SP |  |  |  | 0 | 226 | SP |  |  |  | 0 |  | 226 | 226
42 | IPC4020exp/IPC4022exp | 2 | Phase break | Indication for phase break | SP |  |  |  | 0 | 227 | SP |  |  |  | 0 |  | 227 | 227
43 | IPC4020exp/IPC4022exp | 2 | OC Trip Ind | Indication mirroring the LED OC Trip. | SP |  |  |  | 0 | 228 | SP |  |  |  | 0 |  | 228 | 228
44 | IPC4020exp/IPC4022exp | 2 | EF Trip Ind | Indication mirroring the LED EF Trip. | SP |  |  |  | 0 | 229 | SP |  |  |  | 0 |  | 229 | 229
45 | IPC4020exp/IPC4022exp | 2 | Logical input 1 | Option AR: RECL OFF/ON | DP |  |  |  | 0 | 0 | DP |  |  |  | 0 |  | 0 | 0 |  |  |  | *
46 | IPC4020exp/IPC4022exp | 2 | Logical input 2 | Reserved | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
47 | IPC4020exp/IPC4022exp | 2 | Logical input 3 | Reserved | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
48 | IPC4020exp | 3 | Reserved |  | SP | [5 empty] | SP
49 | IPC4020exp | 3 | Reserved |  | SP | [5 empty] | SP
50 | IPC4020exp | 3 | Reserved |  | SP | [5 empty] | SP
51 | IPC4020exp/IPC4022exp | 3 | OC Start | Overcurrent – START indication | SP |  |  |  | 0 | 320 | SP |  |  |  | 0 |  | 320 | 320
52 | IPC4020exp/IPC4022exp | 3 | OC1 Trip | Overcurrent – TRIP indication, level 1 | SP |  |  |  | 0 | 321 | SP |  |  |  | 0 |  | 321 | 321
53 | IPC4020exp/IPC4022exp | 3 | OC2 Trip | Overcurrent – TRIP indication, level 2 | SP |  |  |  | 0 | 322 | SP |  |  |  | 0 |  | 322 | 322
54 | IPC4020exp/IPC4022exp | 3 | EF Start | Earth fault – START indication | SP |  |  |  | 0 | 323 | SP |  |  |  | 0 |  | 323 | 323
55 | IPC4020exp/IPC4022exp | 3 | EF Trip | Earth fault – TRIP indication | SP |  |  |  | 0 | 324 | SP |  |  |  | 0 |  | 324 | 324
56 | IPC4020exp/IPC4022exp | 3 | EF Start (non-dir.) | Earth fault, non-directional – START indication | SP |  |  |  | 0 | 325 | SP |  |  |  | 0 |  | 325 | 325
57 | IPC4020exp/IPC4022exp | 3 | EF Trip (non-dir.) | Earth fault, non-directional – TRIP indication | SP |  |  |  | 0 | 326 | SP |  |  |  | 0 |  | 326 | 326
58 | IPC4020exp/IPC4022exp | 3 | Phase break | Indication for phase break | SP |  |  |  | 0 | 327 | SP |  |  |  | 0 |  | 327 | 327
59 | IPC4020exp/IPC4022exp | 3 | OC Trip Ind | Indication mirroring the LED OC Trip. | SP |  |  |  | 0 | 328 | SP |  |  |  | 0 |  | 328 | 328
60 | IPC4020exp/IPC4022exp | 3 | EF Trip Ind | Indication mirroring the LED EF Trip. | SP |  |  |  | 0 | 329 | SP |  |  |  | 0 |  | 329 | 329
61 | IPC4020exp/IPC4022exp | 3 | Logical input 1 | Option AR: RECL OFF/ON | DP |  |  |  | 0 | 0 | DP |  |  |  | 0 |  | 0 | 0 |  |  |  | *
62 | IPC4020exp/IPC4022exp | 3 | Logical input 2 | Reserved | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
63 | IPC4020exp/IPC4022exp | 3 | Logical input 3 | Reserved | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
48 | IPC4020exp4-6 | 4 | Reserved |  | SP | [5 empty] | SP
49 | IPC4020exp4-6 | 4 | Reserved |  | SP | [5 empty] | SP
50 | IPC4020exp4-6 | 4 | Reserved |  | SP | [5 empty] | SP
51 | IPC4020exp4-6 | 4 | OC Start | Overcurrent – START indication | SP |  |  |  | 0 | 420 | SP |  |  |  | 0 |  | 420 | 420
52 | IPC4020exp4-6 | 4 | OC1 Trip | Overcurrent – TRIP indication, level 1 | SP |  |  |  | 0 | 421 | SP |  |  |  | 0 |  | 421 | 421
53 | IPC4020exp4-6 | 4 | OC2 Trip | Overcurrent – TRIP indication, level 2 | SP |  |  |  | 0 | 422 | SP |  |  |  | 0 |  | 422 | 422
54 | IPC4020exp4-6 | 4 | EF Start | Earth fault – START indication | SP |  |  |  | 0 | 423 | SP |  |  |  | 0 |  | 423 | 423
55 | IPC4020exp4-6 | 4 | EF Trip | Earth fault – TRIP indication | SP |  |  |  | 0 | 424 | SP |  |  |  | 0 |  | 424 | 424
56 | IPC4020exp4-6 | 4 | EF Start (non-dir.) | Earth fault, non-directional – START indication | SP |  |  |  | 0 | 425 | SP |  |  |  | 0 |  | 425 | 425
57 | IPC4020exp4-6 | 4 | EF Trip (non-dir.) | Earth fault, non-directional – TRIP indication | SP |  |  |  | 0 | 426 | SP |  |  |  | 0 |  | 426 | 426
58 | IPC4020exp4-6 | 4 | Phase break | Indication for phase break | SP |  |  |  | 0 | 427 | SP |  |  |  | 0 |  | 427 | 427
59 | IPC4020exp4-6 | 4 | OC Trip Ind | Indication mirroring the LED OC Trip. | SP |  |  |  | 0 | 428 | SP |  |  |  | 0 |  | 428 | 428
60 | IPC4020exp4-6 | 4 | EF Trip Ind | Indication mirroring the LED EF Trip. | SP |  |  |  | 0 | 429 | SP |  |  |  | 0 |  | 429 | 429
61 | IPC4020exp4-6 | 4 | Logical input 1 | Option AR: RECL OFF/ON | DP |  |  |  | 0 | 0 | DP |  |  |  | 0 |  | 0 | 0 |  |  |  | *
62 | IPC4020exp4-6 | 4 | Logical input 2 | Reserved | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
63 | IPC4020exp4-6 | 4 | Logical input 3 | Reserved | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
48 | IPC4020exp4-6 | 5 | Reserved |  | SP | [5 empty] | SP
49 | IPC4020exp4-6 | 5 | Reserved |  | SP | [5 empty] | SP
50 | IPC4020exp4-6 | 5 | Reserved |  | SP | [5 empty] | SP
51 | IPC4020exp4-6 | 5 | OC Start | Overcurrent – START indication | SP |  |  |  | 0 | 520 | SP |  |  |  | 0 |  | 520 | 520
52 | IPC4020exp4-6 | 5 | OC1 Trip | Overcurrent – TRIP indication, level 1 | SP |  |  |  | 0 | 521 | SP |  |  |  | 0 |  | 521 | 521
53 | IPC4020exp4-6 | 5 | OC2 Trip | Overcurrent – TRIP indication, level 2 | SP |  |  |  | 0 | 522 | SP |  |  |  | 0 |  | 522 | 522
54 | IPC4020exp4-6 | 5 | EF Start | Earth fault – START indication | SP |  |  |  | 0 | 523 | SP |  |  |  | 0 |  | 523 | 523
55 | IPC4020exp4-6 | 5 | EF Trip | Earth fault – TRIP indication | SP |  |  |  | 0 | 524 | SP |  |  |  | 0 |  | 524 | 524
56 | IPC4020exp4-6 | 5 | EF Start (non-dir.) | Earth fault, non-directional – START indication | SP |  |  |  | 0 | 525 | SP |  |  |  | 0 |  | 525 | 525
57 | IPC4020exp4-6 | 5 | EF Trip (non-dir.) | Earth fault, non-directional – TRIP indication | SP |  |  |  | 0 | 526 | SP |  |  |  | 0 |  | 526 | 526
58 | IPC4020exp4-6 | 5 | Phase break | Indication for phase break | SP |  |  |  | 0 | 527 | SP |  |  |  | 0 |  | 527 | 527
59 | IPC4020exp4-6 | 5 | OC Trip Ind | Indication mirroring the LED OC Trip. | SP |  |  |  | 0 | 528 | SP |  |  |  | 0 |  | 528 | 528
60 | IPC4020exp4-6 | 5 | EF Trip Ind | Indication mirroring the LED EF Trip. | SP |  |  |  | 0 | 529 | SP |  |  |  | 0 |  | 529 | 529
61 | IPC4020exp4-6 | 5 | Logical input 1 | Option AR: RECL OFF/ON | DP |  |  |  | 0 | 0 | DP |  |  |  | 0 |  | 0 | 0 |  |  |  | *
62 | IPC4020exp4-6 | 5 | Logical input 2 | Reserved | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
63 | IPC4020exp4-6 | 5 | Logical input 3 | Reserved | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
48 | IPC4020exp4-6 | 6 | Reserved |  | SP | [5 empty] | SP
49 | IPC4020exp4-6 | 6 | Reserved |  | SP | [5 empty] | SP
50 | IPC4020exp4-6 | 6 | Reserved |  | SP | [5 empty] | SP
51 | IPC4020exp4-6 | 6 | OC Start | Overcurrent – START indication | SP |  |  |  | 0 | 620 | SP |  |  |  | 0 |  | 620 | 620
52 | IPC4020exp4-6 | 6 | OC1 Trip | Overcurrent – TRIP indication, level 1 | SP |  |  |  | 0 | 621 | SP |  |  |  | 0 |  | 621 | 621
53 | IPC4020exp4-6 | 6 | OC2 Trip | Overcurrent – TRIP indication, level 2 | SP |  |  |  | 0 | 622 | SP |  |  |  | 0 |  | 622 | 622
54 | IPC4020exp4-6 | 6 | EF Start | Earth fault – START indication | SP |  |  |  | 0 | 623 | SP |  |  |  | 0 |  | 623 | 623
55 | IPC4020exp4-6 | 6 | EF Trip | Earth fault – TRIP indication | SP |  |  |  | 0 | 624 | SP |  |  |  | 0 |  | 624 | 624
56 | IPC4020exp4-6 | 6 | EF Start (non-dir.) | Earth fault, non-directional – START indication | SP |  |  |  | 0 | 625 | SP |  |  |  | 0 |  | 625 | 625
57 | IPC4020exp4-6 | 6 | EF Trip (non-dir.) | Earth fault, non-directional – TRIP indication | SP |  |  |  | 0 | 626 | SP |  |  |  | 0 |  | 626 | 626
58 | IPC4020exp4-6 | 6 | Phase break | Indication for phase break | SP |  |  |  | 0 | 627 | SP |  |  |  | 0 |  | 627 | 627
59 | IPC4020exp4-6 | 6 | OC Trip Ind | Indication mirroring the LED OC Trip. | SP |  |  |  | 0 | 628 | SP |  |  |  | 0 |  | 628 | 628
60 | IPC4020exp4-6 | 6 | EF Trip Ind | Indication mirroring the LED EF Trip. | SP |  |  |  | 0 | 629 | SP |  |  |  | 0 |  | 629 | 629
61 | IPC4020exp4-6 | 6 | Logical input 1 | Option AR: RECL OFF/ON | DP |  |  |  | 0 | 0 | DP |  |  |  | 0 |  | 0 | 0 |  |  |  | *
62 | IPC4020exp4-6 | 6 | Logical input 2 | Reserved | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
63 | IPC4020exp4-6 | 6 | Logical input 3 | Reserved | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
| IPC4020/IPC4020exp | Master | Slave 1 communication error | Connection lost to slave 1 | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
* | IPC4020/IPC4020exp | Master | Slave 2 communication error | Connection lost to slave 2 | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
| IPC4020/IPC4020exp | Master | Slave 3 communication error | Connection lost to slave 3 | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
| IPC4020/IPC4020exp | Master | Slave 4 communication error | Connection lost to slave 4 | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
| IPC4020/IPC4020exp | Master | Slave 5 communication error | Connection lost to slave 5 | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
| IPC4020/IPC4020exp | Master | Slave 6 communication error | Connection lost to slave 6 | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
| IPC4020/IPC4020exp | Master | Slave 7 communication error | Connection lost to slave 7 | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
| IPC4020/IPC4020exp | Master | Slave 8 communication error | Connection lost to slave 8 | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
| IPC4020/IPC4020exp | Master | Slave 9 communication error | Connection lost to slave 9 | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
| IPC4020/IPC4020exp | Master | Slave 10 communication error | Connection lost to slave 10 | SP |  |  |  | 0 | 0 | SP |  |  |  | 0 |  | 0 | 0
Optional setting if the device is equipped with Autoreclosure
Note on G6: SP - Single Point DP - Double Point
Note on M6: SP - Single Point DP - Double Point

## IPC402x Bin OUT objects
[5 empty] | Factory Default Settings |  |  |  |  | Custom Settings | [6 empty] | Circuit Diagram |  | Comissioning
| IPC402x: Binary outputs | [7 empty] | IEC IO Address |  |  |  |  | IEC IO Address |  |  |  |  | Green |  | Revision
Internal input number | Products | Bay | Module output | Comment | Type | Blocked | Direct Execute | Pulse time [ms] | Lower (16 bit) | Type | Blocked | Direct Execute | Pulse time [ms] | Upper (8 bit) | Lower (16 bit) | Decimal | Page | Signal name | lined |  | no | Comment
0 | IPC402x | Common | Ack | Object linked to the ACN button on the front panel | SC |  |  | 100 | 21000 | SC |  |  | 100 |  | 21000 | 21000
1 | IPC402x | Common | Output 1 | Objects linked to physical output 1 | SC |  |  | 100 | 21001 | SC |  |  | 100 |  | 21001 | 21001
2 | IPC402x | Common | Output 2 | Objects linked to physical output 2 | SC |  |  | 100 | 21002 | SC |  |  | 100 |  | 21002 | 21002
3 | IPC402x | Common | Output 3 | Objects linked to physical output 3 | SC |  |  | 100 | 21003 | SC |  |  | 100 |  | 21003 | 21003
4 | IPC4020/IPC4020exp3 | Common | Output 4 | Objects linked to physical output 4 | SC |  |  | 100 | 21004 | SC |  |  | 100 |  | 21004 | 21004
5 | IPC4020/IPC4020exp3 | Common | Output 5 | Objects linked to physical output 5 | SC |  |  | 100 | 21005 | SC |  |  | 100 |  | 21005 | 21005
6 | IPC4020/IPC4020exp3 | Common | Output 6 | Objects linked to physical output 6 | SC |  |  | 100 | 21006 | SC |  |  | 100 |  | 21006 | 21006
7 | IPC4020/IPC4020exp3 | Common | Output 7 | Objects linked to physical output 7 | SC |  |  | 100 | 21007 | SC |  |  | 100 |  | 21007 | 21007
8 | IPC4020/IPC4020exp3 | Common | Output 8 | Objects linked to physical output 8 | SC |  |  | 100 | 21008 | SC |  |  | 100 |  | 21008 | 21008
| IPC4020exp4-6 | Common | Output 9 | Object linked to physical output 9 | SC |  |  | 100 | 21009 | SC |  |  | 100 |  | 21009 | 21009
| IPC4020exp4-6 | Common | Output 10 | Object linked to physical output 10 | SC |  |  | 100 | 21010 | SC |  |  | 100 |  | 21010 | 21010
| IPC4020exp4-6 | Common | Output 11 | Object linked to physical output 11 | SC |  |  | 100 | 21011 | SC |  |  | 100 |  | 21011 | 21011
| IPC4020exp4-6 | Common | Output 12 | Object linked to physical output 12 | SC |  |  | 100 | 21012 | SC |  |  | 100 |  | 21012 | 21012
| IPC4020exp4-6 | Common | Output 13 | Object linked to physical output 13 | SC |  |  | 100 | 21013 | SC |  |  | 100 |  | 21013 | 21013
9
10 | IPC402x | 1 | Logical output 1 | Option AR: RECL OFF/ON | DC |  |  | 100 | 21101 | DC |  |  | 100 |  | 21101 | 21101 |  |  |  | *
11 | IPC402x | 1 | Logical output 2 | Reserved | SC |  |  | 100 | 21102 | SC |  |  | 100 |  | 21102 | 21102
12 | IPC402x | 1 | Logical output 3 | Reserved | SC |  |  | 100 | 21103 | SC |  |  | 100 |  | 21103 | 21103
13 | IPC402x | 1 | Logical output 4 | Reserved | SC |  |  | 100 | 21104 | SC |  |  | 100 |  | 21104 | 21104
14 | IPC402x | 1 | Logical output 5 | Reserved | SC |  |  | 100 | 21105 | SC |  |  | 100 |  | 21105 | 21105
15 | IPC402x | 1 | Logical output 6 | Reserved | SC |  |  | 100 | 21106 | SC |  |  | 100 |  | 21106 | 21106
16 | IPC402x | 1 | Logical output 7 | Reserved | SC |  |  | 100 | 21107 | SC |  |  | 100 |  | 21107 | 21107
17 | IPC402x | 1 | Logical output 8 | Reserved | SC |  |  | 100 | 21108 | SC |  |  | 100 |  | 21108 | 21108
18 | IPC402x | 1 | Logical output 9 | Reserved | SC |  |  | 100 | 21109 | SC |  |  | 100 |  | 21109 | 21109
19 | IPC402x | 1 | Logical output 10 | Reserved | SC |  |  | 100 | 21110 | SC |  |  | 100 |  | 21110 | 21110
20 | IPC402x | 1 | Logical output 11 | Reserved | SC |  |  | 100 | 21111 | SC |  |  | 100 |  | 21111 | 21111
21 | IPC402x | 1 | Logical output 12 | Reserved | SC |  |  | 100 | 21112 | SC |  |  | 100 |  | 21112 | 21112
22 | IPC402x | 1 | Logical output 13 | Reserved | SC |  |  | 100 | 21113 | SC |  |  | 100 |  | 21113 | 21113
23 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
24 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
25 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
26 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
27 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
28 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
29 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
30 | IPC4020exp/IPC4022exp | 2 | Logical output 1 | Option AR: RECL OFF/ON | DC |  |  | 100 | 21201 | DC |  |  | 100 |  | 21201 | 21201 |  |  |  | *
31 | IPC4020exp/IPC4022exp | 2 | Logical output 2 | Reserved | SC |  |  | 100 | 21202 | SC |  |  | 100 |  | 21202 | 21202
32 | IPC4020exp/IPC4022exp | 2 | Logical output 3 | Reserved | SC |  |  | 100 | 21203 | SC |  |  | 100 |  | 21203 | 21203
33 | IPC4020exp/IPC4022exp | 2 | Logical output 4 | Reserved | SC |  |  | 100 | 21204 | SC |  |  | 100 |  | 21204 | 21204
34 | IPC4020exp/IPC4022exp | 2 | Logical output 5 | Reserved | SC |  |  | 100 | 21205 | SC |  |  | 100 |  | 21205 | 21205
35 | IPC4020exp/IPC4022exp | 2 | Logical output 6 | Reserved | SC |  |  | 100 | 21206 | SC |  |  | 100 |  | 21206 | 21206
36 | IPC4020exp/IPC4022exp | 2 | Logical output 7 | Reserved | SC |  |  | 100 | 21207 | SC |  |  | 100 |  | 21207 | 21207
37 | IPC4020exp/IPC4022exp | 2 | Logical output 8 | Reserved | SC |  |  | 100 | 21208 | SC |  |  | 100 |  | 21208 | 21208
38 | IPC4020exp/IPC4022exp | 2 | Logical output 9 | Reserved | SC |  |  | 100 | 21209 | SC |  |  | 100 |  | 21209 | 21209
39 | IPC4020exp/IPC4022exp | 2 | Logical output 10 | Reserved | SC |  |  | 100 | 21210 | SC |  |  | 100 |  | 21210 | 21210
40 | IPC4020exp/IPC4022exp | 2 | Logical output 11 | Reserved | SC |  |  | 100 | 21211 | SC |  |  | 100 |  | 21211 | 21211
41 | IPC4020exp/IPC4022exp | 2 | Logical output 12 | Reserved | SC |  |  | 100 | 21212 | SC |  |  | 100 |  | 21212 | 21212
42 | IPC4020exp/IPC4022exp | 2 | Logical output 13 | Reserved | SC |  |  | 100 | 21213 | SC |  |  | 100 |  | 21213 | 21213
43 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
44 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
45 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
46 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
47 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
48 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
49 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
50 | IPC4020exp/IPC4022exp | 3 | Logical output 1 | Option AR: RECL OFF/ON | DC |  |  | 100 | 21301 | DC |  |  | 100 |  | 21301 | 21301 |  |  |  | *
51 | IPC4020exp/IPC4022exp | 3 | Logical output 2 | Reserved | SC |  |  | 100 | 21302 | SC |  |  | 100 |  | 21302 | 21302
52 | IPC4020exp/IPC4022exp | 3 | Logical output 3 | Reserved | SC |  |  | 100 | 21303 | SC |  |  | 100 |  | 21303 | 21303
53 | IPC4020exp/IPC4022exp | 3 | Logical output 4 | Reserved | SC |  |  | 100 | 21304 | SC |  |  | 100 |  | 21304 | 21304
54 | IPC4020exp/IPC4022exp | 3 | Logical output 5 | Reserved | SC |  |  | 100 | 21305 | SC |  |  | 100 |  | 21305 | 21305
55 | IPC4020exp/IPC4022exp | 3 | Logical output 6 | Reserved | SC |  |  | 100 | 21306 | SC |  |  | 100 |  | 21306 | 21306
56 | IPC4020exp/IPC4022exp | 3 | Logical output 7 | Reserved | SC |  |  | 100 | 21307 | SC |  |  | 100 |  | 21307 | 21307
57 | IPC4020exp/IPC4022exp | 3 | Logical output 8 | Reserved | SC |  |  | 100 | 21308 | SC |  |  | 100 |  | 21308 | 21308
58 | IPC4020exp/IPC4022exp | 3 | Logical output 9 | Reserved | SC |  |  | 100 | 21309 | SC |  |  | 100 |  | 21309 | 21309
59 | IPC4020exp/IPC4022exp | 3 | Logical output 10 | Reserved | SC |  |  | 100 | 21310 | SC |  |  | 100 |  | 21310 | 21310
60 | IPC4020exp/IPC4022exp | 3 | Logical output 11 | Reserved | SC |  |  | 100 | 21311 | SC |  |  | 100 |  | 21311 | 21311
61 | IPC4020exp/IPC4022exp | 3 | Logical output 12 | Reserved | SC |  |  | 100 | 21312 | SC |  |  | 100 |  | 21312 | 21312
62 | IPC4020exp/IPC4022exp | 3 | Logical output 13 | Reserved | SC |  |  | 100 | 21313 | SC |  |  | 100 |  | 21313 | 21313
63 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
64 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
65 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
66 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
67 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
68 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
69 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
70 | IPC4020exp4-6 | 4 | Logical output 1 | Option AR: RECL OFF/ON | DC |  |  | 100 | 21401 | DC |  |  | 100 |  | 21401 | 21401 |  |  |  | *
71 | IPC4020exp4-6 | 4 | Logical output 2 | Reserved | SC |  |  | 100 | 21402 | SC |  |  | 100 |  | 21402 | 21402
72 | IPC4020exp4-6 | 4 | Logical output 3 | Reserved | SC |  |  | 100 | 21403 | SC |  |  | 100 |  | 21403 | 21403
73 | IPC4020exp4-6 | 4 | Logical output 4 | Reserved | SC |  |  | 100 | 21404 | SC |  |  | 100 |  | 21404 | 21404
74 | IPC4020exp4-6 | 4 | Logical output 5 | Reserved | SC |  |  | 100 | 21405 | SC |  |  | 100 |  | 21405 | 21405
75 | IPC4020exp4-6 | 4 | Logical output 6 | Reserved | SC |  |  | 100 | 21406 | SC |  |  | 100 |  | 21406 | 21406
76 | IPC4020exp4-6 | 4 | Logical output 7 | Reserved | SC |  |  | 100 | 21407 | SC |  |  | 100 |  | 21407 | 21407
77 | IPC4020exp4-6 | 4 | Logical output 8 | Reserved | SC |  |  | 100 | 21408 | SC |  |  | 100 |  | 21408 | 21408
78 | IPC4020exp4-6 | 4 | Logical output 9 | Reserved | SC |  |  | 100 | 21409 | SC |  |  | 100 |  | 21409 | 21409
79 | IPC4020exp4-6 | 4 | Logical output 10 | Reserved | SC |  |  | 100 | 21410 | SC |  |  | 100 |  | 21410 | 21410
80 | IPC4020exp4-6 | 4 | Logical output 11 | Reserved | SC |  |  | 100 | 21411 | SC |  |  | 100 |  | 21411 | 21411
81 | IPC4020exp4-6 | 4 | Logical output 12 | Reserved | SC |  |  | 100 | 21412 | SC |  |  | 100 |  | 21412 | 21412
82 | IPC4020exp4-6 | 4 | Logical output 13 | Reserved | SC |  |  | 100 | 21413 | SC |  |  | 100 |  | 21413 | 21413
83 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
84 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
85 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
86 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
87 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
88 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
89 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
90 | IPC4020exp4-6 | 5 | Logical output 1 | Option AR: RECL OFF/ON | DC |  |  | 100 | 21501 | DC |  |  | 100 |  | 21501 | 21501 |  |  |  | *
91 | IPC4020exp4-6 | 5 | Logical output 2 | Reserved | SC |  |  | 100 | 21502 | SC |  |  | 100 |  | 21502 | 21502
92 | IPC4020exp4-6 | 5 | Logical output 3 | Reserved | SC |  |  | 100 | 21503 | SC |  |  | 100 |  | 21503 | 21503
93 | IPC4020exp4-6 | 5 | Logical output 4 | Reserved | SC |  |  | 100 | 21504 | SC |  |  | 100 |  | 21504 | 21504
94 | IPC4020exp4-6 | 5 | Logical output 5 | Reserved | SC |  |  | 100 | 21505 | SC |  |  | 100 |  | 21505 | 21505
95 | IPC4020exp4-6 | 5 | Logical output 6 | Reserved | SC |  |  | 100 | 21506 | SC |  |  | 100 |  | 21506 | 21506
96 | IPC4020exp4-6 | 5 | Logical output 7 | Reserved | SC |  |  | 100 | 21507 | SC |  |  | 100 |  | 21507 | 21507
97 | IPC4020exp4-6 | 5 | Logical output 8 | Reserved | SC |  |  | 100 | 21508 | SC |  |  | 100 |  | 21508 | 21508
98 | IPC4020exp4-6 | 5 | Logical output 9 | Reserved | SC |  |  | 100 | 21509 | SC |  |  | 100 |  | 21509 | 21509
99 | IPC4020exp4-6 | 5 | Logical output 10 | Reserved | SC |  |  | 100 | 21510 | SC |  |  | 100 |  | 21510 | 21510
100 | IPC4020exp4-6 | 5 | Logical output 11 | Reserved | SC |  |  | 100 | 21511 | SC |  |  | 100 |  | 21511 | 21511
101 | IPC4020exp4-6 | 5 | Logical output 12 | Reserved | SC |  |  | 100 | 21512 | SC |  |  | 100 |  | 21512 | 21512
102 | IPC4020exp4-6 | 5 | Logical output 13 | Reserved | SC |  |  | 100 | 21513 | SC |  |  | 100 |  | 21513 | 21513
103 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
104 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
105 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
106 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
107 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
108 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
109 | IPC402x | Common | Reserved |  | SC |  |  |  |  | SC
110 | IPC4020exp4-6 | 6 | Logical output 1 | Option AR: RECL OFF/ON | DC |  |  | 100 | 21601 | DC |  |  | 100 |  | 21601 | 21601 |  |  |  | *
111 | IPC4020exp4-6 | 6 | Logical output 2 | Reserved | SC |  |  | 100 | 21602 | SC |  |  | 100 |  | 21602 | 21602
112 | IPC4020exp4-6 | 6 | Logical output 3 | Reserved | SC |  |  | 100 | 21603 | SC |  |  | 100 |  | 21603 | 21603
113 | IPC4020exp4-6 | 6 | Logical output 4 | Reserved | SC |  |  | 100 | 21604 | SC |  |  | 100 |  | 21604 | 21604
114 | IPC4020exp4-6 | 6 | Logical output 5 | Reserved | SC |  |  | 100 | 21605 | SC |  |  | 100 |  | 21605 | 21605
115 | IPC4020exp4-6 | 6 | Logical output 6 | Reserved | SC |  |  | 100 | 21606 | SC |  |  | 100 |  | 21606 | 21606
116 | IPC4020exp4-6 | 6 | Logical output 7 | Reserved | SC |  |  | 100 | 21607 | SC |  |  | 100 |  | 21607 | 21607
117 | IPC4020exp4-6 | 6 | Logical output 8 | Reserved | SC |  |  | 100 | 21608 | SC |  |  | 100 |  | 21608 | 21608
118 | IPC4020exp4-6 | 6 | Logical output 9 | Reserved | SC |  |  | 100 | 21609 | SC |  |  | 100 |  | 21609 | 21609
119 | IPC4020exp4-6 | 6 | Logical output 10 | Reserved | SC |  |  | 100 | 21610 | SC |  |  | 100 |  | 21610 | 21610
120 | IPC4020exp4-6 | 6 | Logical output 11 | Reserved | SC |  |  | 100 | 21611 | SC |  |  | 100 |  | 21611 | 21611
121 | IPC4020exp4-6 | 6 | Logical output 12 | Reserved | SC |  |  | 100 | 21612 | SC |  |  | 100 |  | 21612 | 21612
122 | IPC4020exp4-6 | 6 | Logical output 13 | Reserved | SC |  |  | 100 | 21613 | SC |  |  | 100 |  | 21613 | 21613
Note on G6: SC - Single Command DC - Double Command
Note on L6: SC - Single Command DC - Double Command

## IPC402x Analog IN objects
[5 empty] | Factory Default Settings | [5 empty] | Custom Settings | [7 empty] | Circuit Diagram |  | Comissioning
| IPC402x: Analog inputs | [8 empty] | IEC IO Address | [5 empty] | IEC IO Address |  |  |  |  | Green | Revision
Internal input number | Products | Bay | Module input | Comment | Type | Blocked | Timetagged | Cyclic | Deadband [%] | Lower (16 bit) | Type | Blocked | Timetagged | Cyclic | Deadband [%] | Upper (8 bit) | Lower (16 bit) | Decimal | Page | Signal name | lined | no | Comment
0 | IPC402x | Common | Unit temperature | Temperature measurement inside the device | Float [SI] |  |  |  | 5.0 | 3001 | Float [SI] |  |  |  | 5.0 |  | 3001 | 3001
1 | IPC402x | Common | Reserved
2 | IPC402x | Common | Reserved
3 | IPC402x | Common | Reserved
4 | IPC402x | Common | Reserved
5 | IPC402x | Common | Reserved
6 | IPC402x | Common | Reserved
7 | IPC402x | Common | Reserved
8 | IPC402x | 1 | L1 Current | Measured current (rms) at input L1 / Ia. | Float [SI] |  |  |  | 10.0 | 3101 | Float [SI] |  |  |  | 10.0 |  | 3101 | 3101
9 | IPC402x | 1 | L2 Current | Measured current (rms) at input L2 / Ib. | Float [SI] |  |  |  | 10.0 | 3102 | Float [SI] |  |  |  | 10.0 |  | 3102 | 3102
10 | IPC402x | 1 | L3 Current | Measured current (rms) at input L3 / Ic. | Float [SI] |  |  |  | 10.0 | 3103 | Float [SI] |  |  |  | 10.0 |  | 3103 | 3103
11 | IPC402x | 1 | LN Current | Calculated residual current 3I0 (rms) | Float [SI] |  |  |  | 1.0 | 3104 | Float [SI] |  |  |  | 1.0 |  | 3104 | 3104
12 | IPC402x | 1 | Max Fault Current | Maximum fault current (rms), I>/I>> | Float [SI] |  |  |  | N/A | 3105 | Float [SI] |  |  |  | N/A |  | 3105 | 3105
13 | IPC402x | 1 | Max Current | Maximum current (rms) | Float [SI] |  |  |  | 10.0 | 3106 | Float [SI] |  |  |  | 10.0 |  | 3106 | 3106
14 | IPC402x | 1 | Avg Current Period | Average current value (rms), 15 min | Float [SI] |  |  |  | 10.0 | 3107 | Float [SI] |  |  |  | 10.0 |  | 3107 | 3107
15 | IPC402x | 1 | Fault phase | Faulty phase / phases | Scaled [SI*1] |  |  |  | N/A | 3108 | Scaled [SI*1] |  |  |  | N/A |  | 3108 | 3108
16 | IPC4020exp/IPC4022exp | 2 | L1 Current | Measured current (rms) at input L1 / Ia. | Float [SI] |  |  |  | 10.0 | 3201 | Float [SI] |  |  |  | 10.0 |  | 3201 | 3201
17 | IPC4020exp/IPC4022exp | 2 | L2 Current | Measured current (rms) at input L2 / Ib. | Float [SI] |  |  |  | 10.0 | 3202 | Float [SI] |  |  |  | 10.0 |  | 3202 | 3202
18 | IPC4020exp/IPC4022exp | 2 | L3 Current | Measured current (rms) at input L3 / Ic. | Float [SI] |  |  |  | 10.0 | 3203 | Float [SI] |  |  |  | 10.0 |  | 3203 | 3203
19 | IPC4020exp/IPC4022exp | 2 | LN Current | Calculated residual current 3I0 (rms) | Float [SI] |  |  |  | 1.0 | 3204 | Float [SI] |  |  |  | 1.0 |  | 3204 | 3204
20 | IPC4020exp/IPC4022exp | 2 | Max Fault Current | Maximum fault current (rms), I>/I>> | Float [SI] |  |  |  | N/A | 3205 | Float [SI] |  |  |  | N/A |  | 3205 | 3205
21 | IPC4020exp/IPC4022exp | 2 | Max Current | Maximum current (rms) | Float [SI] |  |  |  | 10.0 | 3206 | Float [SI] |  |  |  | 10.0 |  | 3206 | 3206
22 | IPC4020exp/IPC4022exp | 2 | Avg Current Period | Average current value (rms), 15 min | Float [SI] |  |  |  | 10.0 | 3207 | Float [SI] |  |  |  | 10.0 |  | 3207 | 3207
23 | IPC4020exp/IPC4022exp | 2 | Fault phase | Faulty phase / phases | Scaled [SI*1] |  |  |  | N/A | 3208 | Scaled [SI*1] |  |  |  | N/A |  | 3208 | 3208
24 | IPC4020exp/IPC4022exp | 3 | L1 Current | Measured current (rms) at input L1 / Ia. | Float [SI] |  |  |  | 10.0 | 3301 | Float [SI] |  |  |  | 10.0 |  | 3301 | 3301
25 | IPC4020exp/IPC4022exp | 3 | L2 Current | Measured current (rms) at input L2 / Ib. | Float [SI] |  |  |  | 10.0 | 3302 | Float [SI] |  |  |  | 10.0 |  | 3302 | 3302
26 | IPC4020exp/IPC4022exp | 3 | L3 Current | Measured current (rms) at input L3 / Ic. | Float [SI] |  |  |  | 10.0 | 3303 | Float [SI] |  |  |  | 10.0 |  | 3303 | 3303
27 | IPC4020exp/IPC4022exp | 3 | LN Current | Calculated residual current 3I0 (rms) | Float [SI] |  |  |  | 1.0 | 3304 | Float [SI] |  |  |  | 1.0 |  | 3304 | 3304
28 | IPC4020exp/IPC4022exp | 3 | Max Fault Current | Maximum fault current (rms), I>/I>> | Float [SI] |  |  |  | N/A | 3305 | Float [SI] |  |  |  | N/A |  | 3305 | 3305
29 | IPC4020exp/IPC4022exp | 3 | Max Current | Maximum current (rms) | Float [SI] |  |  |  | 10.0 | 3306 | Float [SI] |  |  |  | 10.0 |  | 3306 | 3306
30 | IPC4020exp/IPC4022exp | 3 | Avg Current Period | Average current value (rms), 15 min | Float [SI] |  |  |  | 10.0 | 3307 | Float [SI] |  |  |  | 10.0 |  | 3307 | 3307
31 | IPC4020exp/IPC4022exp | 3 | Fault phase | Faulty phase / phases | Scaled [SI*1] |  |  |  | N/A | 3308 | Scaled [SI*1] |  |  |  | N/A |  | 3308 | 3308
| IPC4020exp4-6 | 4 | L1 Current | Measured current (rms) at input L1 / Ia. | Float [SI] |  |  |  | 10.0 | 3401 | Float [SI] |  |  |  | 10.0 |  | 3401 | 3401
| IPC4020exp4-6 | 4 | L2 Current | Measured current (rms) at input L2 / Ib. | Float [SI] |  |  |  | 10.0 | 3402 | Float [SI] |  |  |  | 10.0 |  | 3402 | 3402
| IPC4020exp4-6 | 4 | L3 Current | Measured current (rms) at input L3 / Ic. | Float [SI] |  |  |  | 10.0 | 3403 | Float [SI] |  |  |  | 10.0 |  | 3403 | 3403
| IPC4020exp4-6 | 4 | LN Current | Calculated residual current 3I0 (rms) | Float [SI] |  |  |  | 1.0 | 3404 | Float [SI] |  |  |  | 1.0 |  | 3404 | 3404
| IPC4020exp4-6 | 4 | Max Fault Current | Maximum fault current (rms), I>/I>> | Float [SI] |  |  |  | N/A | 3405 | Float [SI] |  |  |  | N/A |  | 3405 | 3405
| IPC4020exp4-6 | 4 | Max Current | Maximum current (rms) | Float [SI] |  |  |  | 10.0 | 3406 | Float [SI] |  |  |  | 10.0 |  | 3406 | 3406
| IPC4020exp4-6 | 4 | Avg Current Period | Average current value (rms), 15 min | Float [SI] |  |  |  | 10.0 | 3407 | Float [SI] |  |  |  | 10.0 |  | 3407 | 3407
| IPC4020exp4-6 | 4 | Fault phase | Faulty phase / phases | Scaled [SI*1] |  |  |  | N/A | 3408 | Scaled [SI*1] |  |  |  | N/A |  | 3408 | 3408
| IPC4020exp4-6 | 5 | L1 Current | Measured current (rms) at input L1 / Ia. | Float [SI] |  |  |  | 10.0 | 3501 | Float [SI] |  |  |  | 10.0 |  | 3501 | 3501
| IPC4020exp4-6 | 5 | L2 Current | Measured current (rms) at input L2 / Ib. | Float [SI] |  |  |  | 10.0 | 3502 | Float [SI] |  |  |  | 10.0 |  | 3502 | 3502
| IPC4020exp4-6 | 5 | L3 Current | Measured current (rms) at input L3 / Ic. | Float [SI] |  |  |  | 10.0 | 3503 | Float [SI] |  |  |  | 10.0 |  | 3503 | 3503
| IPC4020exp4-6 | 5 | LN Current | Calculated residual current 3I0 (rms) | Float [SI] |  |  |  | 1.0 | 3504 | Float [SI] |  |  |  | 1.0 |  | 3504 | 3504
| IPC4020exp4-6 | 5 | Max Fault Current | Maximum fault current (rms), I>/I>> | Float [SI] |  |  |  | N/A | 3505 | Float [SI] |  |  |  | N/A |  | 3505 | 3505
| IPC4020exp4-6 | 5 | Max Current | Maximum current (rms) | Float [SI] |  |  |  | 10.0 | 3506 | Float [SI] |  |  |  | 10.0 |  | 3506 | 3506
| IPC4020exp4-6 | 5 | Avg Current Period | Average current value (rms), 15 min | Float [SI] |  |  |  | 10.0 | 3507 | Float [SI] |  |  |  | 10.0 |  | 3507 | 3507
| IPC4020exp4-6 | 5 | Fault phase | Faulty phase / phases | Scaled [SI*1] |  |  |  | N/A | 3508 | Scaled [SI*1] |  |  |  | N/A |  | 3508 | 3508
| IPC4020exp4-6 | 6 | L1 Current | Measured current (rms) at input L1 / Ia. | Float [SI] |  |  |  | 10.0 | 3601 | Float [SI] |  |  |  | 10.0 |  | 3601 | 3601
| IPC4020exp4-6 | 6 | L2 Current | Measured current (rms) at input L2 / Ib. | Float [SI] |  |  |  | 10.0 | 3602 | Float [SI] |  |  |  | 10.0 |  | 3602 | 3602
| IPC4020exp4-6 | 6 | L3 Current | Measured current (rms) at input L3 / Ic. | Float [SI] |  |  |  | 10.0 | 3603 | Float [SI] |  |  |  | 10.0 |  | 3603 | 3603
| IPC4020exp4-6 | 6 | LN Current | Calculated residual current 3I0 (rms) | Float [SI] |  |  |  | 1.0 | 3604 | Float [SI] |  |  |  | 1.0 |  | 3604 | 3604
| IPC4020exp4-6 | 6 | Max Fault Current | Maximum fault current (rms), I>/I>> | Float [SI] |  |  |  | N/A | 3605 | Float [SI] |  |  |  | N/A |  | 3605 | 3605
| IPC4020exp4-6 | 6 | Max Current | Maximum current (rms) | Float [SI] |  |  |  | 10.0 | 3606 | Float [SI] |  |  |  | 10.0 |  | 3606 | 3606
| IPC4020exp4-6 | 6 | Avg Current Period | Average current value (rms), 15 min | Float [SI] |  |  |  | 10.0 | 3607 | Float [SI] |  |  |  | 10.0 |  | 3607 | 3607
| IPC4020exp4-6 | 6 | Fault phase | Faulty phase / phases | Scaled [SI*1] |  |  |  | N/A | 3608 | Scaled [SI*1] |  |  |  | N/A |  | 3608 | 3608

## PDCIO Bin IN objects
[5 empty] | Factory Default Settings | [5 empty] | Custom Settings | [7 empty] | Circuit Diagram |  | Comissioning
| PDCIO: Binary inputs | [8 empty] | IEC IO Address | [5 empty] | IEC IO Address |  |  |  |  | Green |  | Revision
Internal input number | Products | Module | Module input | Comment | Type | Blocked | Negative | Timetagged | Delay [ms] | Lower (16 bit) | Type | Blocked | Negative | Timetagged | Delay [ms] | Upper (8 bit) | Lower (16 bit) | Decimal | Page | Signal name | lined |  | no | Comment
0 | PDCIO | PDCIO | Ack button | Object linked to the ACN button on the front panel | SP |  |  |  | 0 | 1000 | SP |  |  |  | 0 |  | 1000 | 1000
1 | PDCIO | PDCIO | Input 1 | Object linked to physical input 1 | SP |  |  |  | 0 | 1001 | SP |  |  |  | 0 |  | 1001 | 1001
2 | PDCIO | PDCIO | Input 2 | Object linked to physical input 2 | SP |  |  |  | 0 | 1002 | SP |  |  |  | 0 |  | 1002 | 1002
3 | PDCIO | PDCIO | Input 3 | Object linked to physical input 3 | SP |  |  |  | 0 | 1003 | SP |  |  |  | 0 |  | 1003 | 1003
4 | PDCIO | PDCIO | Input 4 | Object linked to physical input 4 | SP |  |  |  | 0 | 1004 | SP |  |  |  | 0 |  | 1004 | 1004
5 | PDCIO | PDCIO | Input 5 | Object linked to physical input 5 | SP |  |  |  | 0 | 1005 | SP |  |  |  | 0 |  | 1005 | 1005
6 | PDCIO | PDCIO | Input 6 | Object linked to physical input 6 | SP |  |  |  | 0 | 1006 | SP |  |  |  | 0 |  | 1006 | 1006
7 | PDCIO | PDCIO | Input 7 | Object linked to physical input 7 | SP |  |  |  | 0 | 1007 | SP |  |  |  | 0 |  | 1007 | 1007
| PDCIO | PDCIO | Input 8 | Object linked to physical input 8 | SP |  |  |  | 0 | 1008 | SP |  |  |  | 0 |  | 1008 | 1008
| PDCIO | PDCIO | Input 9 | Object linked to physical input 9 | SP |  |  |  | 0 | 1009 | SP |  |  |  | 0 |  | 1009 | 1009
| PDCIO | PDCIO | Input 10 | Object linked to physical input 10 | SP |  |  |  | 0 | 1010 | SP |  |  |  | 0 |  | 1010 | 1010
| PDCIO | PDCIO | Input 11 | Object linked to physical input 11 | SP |  |  |  | 0 | 1011 | SP |  |  |  | 0 |  | 1011 | 1011
| PDCIO | PDCIO | Input 12 | Object linked to physical input 12 | SP |  |  |  | 0 | 1012 | SP |  |  |  | 0 |  | 1012 | 1012
8 | PDCIO | PDCIO | Input 13 | Object linked to physical input 13 | SP |  |  |  | 0 | 1013 | SP |  |  |  | 0 |  | 1013 | 1013
9 | PDCIO | PDCIO | IRF | Indication for internal error | SP |  |  |  | 0 | 1014 | SP |  |  |  | 0 |  | 1014 | 1014
10 | PDCIO | PDCIO | PT100 High Level 1 | High temperature alarm 1 | SP |  |  |  | 0 | 1015 | SP |  |  |  | 0 |  | 1015 | 1015
11 | PDCIO | PDCIO | PT100 High Level 2 | High temperature alarm 2 | SP |  |  |  | 0 | 1016 | SP |  |  |  | 0 |  | 1016 | 1016
| PDCIO | PDCIO | PT100 Low Level | Low temperature alarm | SP |  |  |  | 0 | 1017 | SP |  |  |  | 0 |  | 1017 | 1017
12 | PDCIO | PDCIO | Low voltage alarm | Option: Battery level under alarm level | SP |  |  |  | 0 | 1020 | SP |  |  |  | 0 |  | 1020 | 1020 |  |  |  | *
13 | PDCIO | PDCIO | Discharge alarm | Option: One minute to activation of discharge protection | SP |  |  |  | 0 | 1021 | SP |  |  |  | 0 |  | 1021 | 1021 |  |  |  | *
14 | PDCIO | PDCIO | Battery test in progress | Option: Battery test in progress | SP |  |  |  | 0 | 1022 | SP |  |  |  | 0 |  | 1022 | 1022 |  |  |  | *
15 | PDCIO | PDCIO | Battery fault | Option: Fault indication after battery test | SP |  |  |  | 0 | 1023 | SP |  |  |  | 0 |  | 1023 | 1023 |  |  |  | *
34
#REF! | PDCIO | PBI 1 | Input 1 | Object connected to physical input 1 | SP |  |  |  | 0 | 1101 | SP |  |  |  | 0 |  | 1101 | 1101
#REF! | PDCIO | PBI 1 | Input 2 | Object connected to physical input 2 | SP |  |  |  | 0 | 1102 | SP |  |  |  | 0 |  | 1102 | 1102
#REF! | PDCIO | PBI 1 | Input 3 | Object connected to physical input 3 | SP |  |  |  | 0 | 1103 | SP |  |  |  | 0 |  | 1103 | 1103
#REF! | PDCIO | PBI 1 | Input 4 | Object connected to physical input 4 | SP |  |  |  | 0 | 1104 | SP |  |  |  | 0 |  | 1104 | 1104
#REF! | PDCIO | PBI 1 | Input 5 | Object connected to physical input 5 | SP |  |  |  | 0 | 1105 | SP |  |  |  | 0 |  | 1105 | 1105
#REF! | PDCIO | PBI 1 | Input 6 | Object connected to physical input 6 | SP |  |  |  | 0 | 1106 | SP |  |  |  | 0 |  | 1106 | 1106
#REF! | PDCIO | PBI 1 | Input 7 | Object connected to physical input 7 | SP |  |  |  | 0 | 1107 | SP |  |  |  | 0 |  | 1107 | 1107
#REF! | PDCIO | PBI 1 | Input 8 | Object connected to physical input 8 | SP |  |  |  | 0 | 1108 | SP |  |  |  | 0 |  | 1108 | 1108
#REF! | PDCIO | PBI 1 | Input 9 | Object connected to physical input 9 | SP |  |  |  | 0 | 1109 | SP |  |  |  | 0 |  | 1109 | 1109
#REF! | PDCIO | PBI 1 | Input 10 | Object connected to physical input 10 | SP |  |  |  | 0 | 1110 | SP |  |  |  | 0 |  | 1110 | 1110
#REF! | PDCIO | PBI 1 | Input 11 | Object connected to physical input 11 | SP |  |  |  | 0 | 1111 | SP |  |  |  | 0 |  | 1111 | 1111
#REF! | PDCIO | PBI 1 | Input 12 | Object connected to physical input 12 | SP |  |  |  | 0 | 1112 | SP |  |  |  | 0 |  | 1112 | 1112
#REF! | PDCIO | PBI 1 | Input 13 | Object connected to physical input 13 | SP |  |  |  | 0 | 1113 | SP |  |  |  | 0 |  | 1113 | 1113
| PDCIO | PBI 1 | Input 14 | Object connected to physical input 14 | SP |  |  |  | 0 | 1114 | SP |  |  |  | 0 |  | 1114 | 1114
| PDCIO | PBI 1 | Input 15 | Object connected to physical input 15 | SP |  |  |  | 0 | 1115 | SP |  |  |  | 0 |  | 1115 | 1115
32 | IPC4020exp | 2 | Reserved
33 | IPC4020exp | 2 | Reserved
34
35 | PDCIO | PBI 2 | Input 1 | Object connected to physical input 1 | SP |  |  |  | 0 | 1201 | SP |  |  |  | 0 |  | 1201 | 1201
36 | PDCIO | PBI 2 | Input 2 | Object connected to physical input 2 | SP |  |  |  | 0 | 1202 | SP |  |  |  | 0 |  | 1202 | 1202
37 | PDCIO | PBI 2 | Input 3 | Object connected to physical input 3 | SP |  |  |  | 0 | 1203 | SP |  |  |  | 0 |  | 1203 | 1203
38 | PDCIO | PBI 2 | Input 4 | Object connected to physical input 4 | SP |  |  |  | 0 | 1204 | SP |  |  |  | 0 |  | 1204 | 1204
39 | PDCIO | PBI 2 | Input 5 | Object connected to physical input 5 | SP |  |  |  | 0 | 1205 | SP |  |  |  | 0 |  | 1205 | 1205
40 | PDCIO | PBI 2 | Input 6 | Object connected to physical input 6 | SP |  |  |  | 0 | 1206 | SP |  |  |  | 0 |  | 1206 | 1206
41 | PDCIO | PBI 2 | Input 7 | Object connected to physical input 7 | SP |  |  |  | 0 | 1207 | SP |  |  |  | 0 |  | 1207 | 1207
42 | PDCIO | PBI 2 | Input 8 | Object connected to physical input 8 | SP |  |  |  | 0 | 1208 | SP |  |  |  | 0 |  | 1208 | 1208
43 | PDCIO | PBI 2 | Input 9 | Object connected to physical input 9 | SP |  |  |  | 0 | 1209 | SP |  |  |  | 0 |  | 1209 | 1209
44 | PDCIO | PBI 2 | Input 10 | Object connected to physical input 10 | SP |  |  |  | 0 | 1210 | SP |  |  |  | 0 |  | 1210 | 1210
45 | PDCIO | PBI 2 | Input 11 | Object connected to physical input 11 | SP |  |  |  | 0 | 1211 | SP |  |  |  | 0 |  | 1211 | 1211
46 | PDCIO | PBI 2 | Input 12 | Object connected to physical input 12 | SP |  |  |  | 0 | 1212 | SP |  |  |  | 0 |  | 1212 | 1212
47 | PDCIO | PBI 2 | Input 13 | Object connected to physical input 13 | SP |  |  |  | 0 | 1213 | SP |  |  |  | 0 |  | 1213 | 1213
48 | PDCIO | PBI 2 | Input 14 | Object connected to physical input 14 | SP |  |  |  | 0 | 1214 | SP |  |  |  | 0 |  | 1214 | 1214
49 | PDCIO | PBI 2 | Input 15 | Object connected to physical input 15 | SP |  |  |  | 0 | 1215 | SP |  |  |  | 0 |  | 1215 | 1215
34
#REF! | PDCIO | PBI 3 | Input 1 | Object connected to physical input 1 | SP |  |  |  | 0 | 1301 | SP |  |  |  | 0 |  | 1301 | 1301
#REF! | PDCIO | PBI 3 | Input 2 | Object connected to physical input 2 | SP |  |  |  | 0 | 1302 | SP |  |  |  | 0 |  | 1302 | 1302
#REF! | PDCIO | PBI 3 | Input 3 | Object connected to physical input 3 | SP |  |  |  | 0 | 1303 | SP |  |  |  | 0 |  | 1303 | 1303
#REF! | PDCIO | PBI 3 | Input 4 | Object connected to physical input 4 | SP |  |  |  | 0 | 1304 | SP |  |  |  | 0 |  | 1304 | 1304
#REF! | PDCIO | PBI 3 | Input 5 | Object connected to physical input 5 | SP |  |  |  | 0 | 1305 | SP |  |  |  | 0 |  | 1305 | 1305
#REF! | PDCIO | PBI 3 | Input 6 | Object connected to physical input 6 | SP |  |  |  | 0 | 1306 | SP |  |  |  | 0 |  | 1306 | 1306
#REF! | PDCIO | PBI 3 | Input 7 | Object connected to physical input 7 | SP |  |  |  | 0 | 1307 | SP |  |  |  | 0 |  | 1307 | 1307
#REF! | PDCIO | PBI 3 | Input 8 | Object connected to physical input 8 | SP |  |  |  | 0 | 1308 | SP |  |  |  | 0 |  | 1308 | 1308
#REF! | PDCIO | PBI 3 | Input 9 | Object connected to physical input 9 | SP |  |  |  | 0 | 1309 | SP |  |  |  | 0 |  | 1309 | 1309
#REF! | PDCIO | PBI 3 | Input 10 | Object connected to physical input 10 | SP |  |  |  | 0 | 1310 | SP |  |  |  | 0 |  | 1310 | 1310
#REF! | PDCIO | PBI 3 | Input 11 | Object connected to physical input 11 | SP |  |  |  | 0 | 1311 | SP |  |  |  | 0 |  | 1311 | 1311
#REF! | PDCIO | PBI 3 | Input 12 | Object connected to physical input 12 | SP |  |  |  | 0 | 1312 | SP |  |  |  | 0 |  | 1312 | 1312
#REF! | PDCIO | PBI 3 | Input 13 | Object connected to physical input 13 | SP |  |  |  | 0 | 1313 | SP |  |  |  | 0 |  | 1313 | 1313
| PDCIO | PBI 3 | Input 14 | Object connected to physical input 14 | SP |  |  |  | 0 | 1314 | SP |  |  |  | 0 |  | 1314 | 1314
* | PDCIO | PBI 3 | Input 15 | Object connected to physical input 15 | SP |  |  |  | 0 | 1315 | SP |  |  |  | 0 |  | 1315 | 1315
* These objects are not available when option Battery Supervision is enabled.
Gäller fr o m IPC firmware version 1-1.0.2
Note on G6: SP - Single Point DP - Double Point
Note on M6: SP - Single Point DP - Double Point

## PDCIO Bin OUT objects
[5 empty] | Factory Default Settings |  |  |  |  | Custom Settings | [6 empty] | Circuit Diagram |  | Comissioning
| PDCIO: Binary outputs | [7 empty] | IEC IO Address |  |  |  |  | IEC IO Address |  |  |  |  | Green |  | Revision
Internal input number | Products | Module | Module output | Comment | Type | Blocked | Direct Execute | Pulse time [ms] | Lower (16 bit) | Type | Blocked | Direct Execute | Pulse time [ms] | Upper (8 bit) | Lower (16 bit) | Decimal | Page | Signal name | lined |  | no | Comment
0 | PDCIO | PDCIO | Ack | Object linked to the ACN button on the front panel | SC |  |  | 200 | 22000 | SC |  |  | 200 |  | 22000 | 22000
1 | PDCIO | PDCIO | Output 1 | Objects linked to physical output 1 | SC |  |  | 100 | 22001 | SC |  |  | 100 |  | 22001 | 22001
2 | PDCIO | PDCIO | Output 2 | Objects linked to physical output 2 | SC |  |  | 100 | 22002 | SC |  |  | 100 |  | 22002 | 22002
3 | PDCIO | PDCIO | Output 3 | Objects linked to physical output 3 | SC |  |  | 100 | 22003 | SC |  |  | 100 |  | 22003 | 22003
4 | PDCIO | PDCIO | Output 4 | Objects linked to physical output 4 | SC |  |  | 100 | 22004 | SC |  |  | 100 |  | 22004 | 22004
| PDCIO | PDCIO | Output 5 | Objects linked to physical output 5 | SC |  |  | 100 | 22005 | SC |  |  | 100 |  | 22005 | 22005
| PDCIO | PDCIO | Output 6 | Objects linked to physical output 6 | SC |  |  | 100 | 22006 | SC |  |  | 100 |  | 22006 | 22006
| PDCIO | PDCIO | Output 7 | Objects linked to physical output 7 | SC |  |  | 100 | 22007 | SC |  |  | 100 |  | 22007 | 22007
| PDCIO | PDCIO | Output 8 | Objects linked to physical output 8 | SC |  |  | 100 | 22008 | SC |  |  | 100 |  | 22008 | 22008
1
| PDCIO | PDCIO | Start battery test | Option: Activation of battery test | SC |  |  | 100 | 22020 | SC |  |  | 100 |  | 22020 | 22020 |  |  |  | *
| PDCIO | PBO 1 | Output 1 | Object connected to physical output 1 | SC |  |  | 100 | 22101 | SC |  |  | 100 |  | 22101 | 22101
| PDCIO | PBO 1 | Output 2 | Object connected to physical output 2 | SC |  |  | 100 | 22102 | SC |  |  | 100 |  | 22102 | 22102
| PDCIO | PBO 1 | Output 3 | Object connected to physical output 3 | SC |  |  | 100 | 22103 | SC |  |  | 100 |  | 22103 | 22103
| PDCIO | PBO 1 | Output 4 | Object connected to physical output 4 | SC |  |  | 100 | 22104 | SC |  |  | 100 |  | 22104 | 22104
| PDCIO | PBO 1 | Output 5 | Object connected to physical output 5 | SC |  |  | 100 | 22105 | SC |  |  | 100 |  | 22105 | 22105
| PDCIO | PBO 1 | Output 6 | Object connected to physical output 6 | SC |  |  | 100 | 22106 | SC |  |  | 100 |  | 22106 | 22106
| PDCIO | PBO 1 | Output 7 | Object connected to physical output 7 | SC |  |  | 100 | 22107 | SC |  |  | 100 |  | 22107 | 22107
| PDCIO | PBO 1 | Output 8 | Object connected to physical output 8 | SC |  |  | 100 | 22108 | SC |  |  | 100 |  | 22108 | 22108
| PDCIO | PBO 1 | Output 9 | Object connected to physical output 9 | SC |  |  | 100 | 22109 | SC |  |  | 100 |  | 22109 | 22109
| PDCIO | PBO 1 | Output 10 | Object connected to physical output 10 | SC |  |  | 100 | 22110 | SC |  |  | 100 |  | 22110 | 22110
| PDCIO | PBO 1 | Output 11 | Object connected to physical output 11 | SC |  |  | 100 | 22111 | SC |  |  | 100 |  | 22111 | 22111
| PDCIO | PBO 1 | Output 12 | Object connected to physical output 12 | SC |  |  | 100 | 22112 | SC |  |  | 100 |  | 22112 | 22112
| PDCIO | PBO 2 | Output 1 | Object connected to physical output 1 | SC |  |  | 100 | 22201 | SC |  |  | 100 |  | 22201 | 22201
| PDCIO | PBO 2 | Output 2 | Object connected to physical output 2 | SC |  |  | 100 | 22202 | SC |  |  | 100 |  | 22202 | 22202
| PDCIO | PBO 2 | Output 3 | Object connected to physical output 3 | SC |  |  | 100 | 22203 | SC |  |  | 100 |  | 22203 | 22203
| PDCIO | PBO 2 | Output 4 | Object connected to physical output 4 | SC |  |  | 100 | 22204 | SC |  |  | 100 |  | 22204 | 22204
| PDCIO | PBO 2 | Output 5 | Object connected to physical output 5 | SC |  |  | 100 | 22205 | SC |  |  | 100 |  | 22205 | 22205
| PDCIO | PBO 2 | Output 6 | Object connected to physical output 6 | SC |  |  | 100 | 22206 | SC |  |  | 100 |  | 22206 | 22206
| PDCIO | PBO 2 | Output 7 | Object connected to physical output 7 | SC |  |  | 100 | 22207 | SC |  |  | 100 |  | 22207 | 22207
| PDCIO | PBO 2 | Output 8 | Object connected to physical output 8 | SC |  |  | 100 | 22208 | SC |  |  | 100 |  | 22208 | 22208
| PDCIO | PBO 2 | Output 9 | Object connected to physical output 9 | SC |  |  | 100 | 22209 | SC |  |  | 100 |  | 22209 | 22209
| PDCIO | PBO 2 | Output 10 | Object connected to physical output 10 | SC |  |  | 100 | 22210 | SC |  |  | 100 |  | 22210 | 22210
| PDCIO | PBO 2 | Output 11 | Object connected to physical output 11 | SC |  |  | 100 | 22211 | SC |  |  | 100 |  | 22211 | 22211
| PDCIO | PBO 2 | Output 12 | Object connected to physical output 12 | SC |  |  | 100 | 22212 | SC |  |  | 100 |  | 22212 | 22212
| PDCIO | PBO 3 | Output 1 | Object connected to physical output 1 | SC |  |  | 100 | 22301 | SC |  |  | 100 |  | 22301 | 22301
| PDCIO | PBO 3 | Output 2 | Object connected to physical output 2 | SC |  |  | 100 | 22302 | SC |  |  | 100 |  | 22302 | 22302
| PDCIO | PBO 3 | Output 3 | Object connected to physical output 3 | SC |  |  | 100 | 22303 | SC |  |  | 100 |  | 22303 | 22303
| PDCIO | PBO 3 | Output 4 | Object connected to physical output 4 | SC |  |  | 100 | 22304 | SC |  |  | 100 |  | 22304 | 22304
| PDCIO | PBO 3 | Output 5 | Object connected to physical output 5 | SC |  |  | 100 | 22305 | SC |  |  | 100 |  | 22305 | 22305
| PDCIO | PBO 3 | Output 6 | Object connected to physical output 6 | SC |  |  | 100 | 22306 | SC |  |  | 100 |  | 22306 | 22306
| PDCIO | PBO 3 | Output 7 | Object connected to physical output 7 | SC |  |  | 100 | 22307 | SC |  |  | 100 |  | 22307 | 22307
| PDCIO | PBO 3 | Output 8 | Object connected to physical output 8 | SC |  |  | 100 | 22308 | SC |  |  | 100 |  | 22308 | 22308
| PDCIO | PBO 3 | Output 9 | Object connected to physical output 9 | SC |  |  | 100 | 22309 | SC |  |  | 100 |  | 22309 | 22309
| PDCIO | PBO 3 | Output 10 | Object connected to physical output 10 | SC |  |  | 100 | 22310 | SC |  |  | 100 |  | 22310 | 22310
| PDCIO | PBO 3 | Output 11 | Object connected to physical output 11 | SC |  |  | 100 | 22311 | SC |  |  | 100 |  | 22311 | 22311
| PDCIO | PBO 3 | Output 12 | Object connected to physical output 12 | SC |  |  | 100 | 22312 | SC |  |  | 100 |  | 22312 | 22312
* These objects are not available when option Battery Supervision is enabled.
Gäller fr o m IPC firmware version 1-1.0.2
Note on G6: SC - Single Command DC - Double Command
Note on L6: SC - Single Command DC - Double Command

## PDCIO Analog IN objects
[5 empty] | Factory Default Settings | [6 empty] | Custom Settings | [8 empty] | Circuit Diagram |  | Comissioning
| IPC402x: Analog inputs | [9 empty] | IEC IO Address | [6 empty] | IEC IO Address |  |  |  |  | Green |  | Revision
Internal input number | Products | Module | Module input | Comment | Type | Blocked | Timetagged | Cyclic | 4-20 mA | Deadband [%] | Lower (16 bit) | Type | Blocked | Timetagged | Cyclic | 4-20 mA | Deadband [%] | Upper (8 bit) | Lower (16 bit) | Decimal | Page | Signal name | lined |  | no | Comment
| PDCIO | PDCIO | Unit temperature | Temperature measurement inside the device | Float [SI] |  |  |  |  | 5.0 | 4001 | Float [SI] |  |  |  |  | 5.0 |  | 4001 | 4001
| PDCIO | PDCIO | PT100 input | Object connected to PT100 input | Float [SI] |  |  |  |  | 5.0 | 4002 | Float [SI] |  |  |  |  | 5.0 |  | 4002 | 4002
| PDCIO | PDCIO | Battery capacity | Calculated battery capacity based on last test | Float [SI] |  |  |  |  | 10.0 | 4020 | Float [SI] |  |  |  |  | 10.0 |  | 4020 | 4020 |  |  |  | *
| PDCIO | PDCIO | Battery voltage | Measured voltage, actual battery voltage | Float [SI] |  |  |  |  | 10.0 | 4021 | Float [SI] |  |  |  |  | 10.0 |  | 4021 | 4021 |  |  |  | *
0 | PDCIO | PAI 1 | Input 1 | Object connected to physical input 1 | Float [SI] |  |  |  |  | 10.0 | 4101 | Float [SI] |  |  |  |  | 10.0 |  | 4101 | 4101
1 | PDCIO | PAI 1 | Input 2 | Object connected to physical input 2 | Float [SI] |  |  |  |  | 10.0 | 4102 | Float [SI] |  |  |  |  | 10.0 |  | 4102 | 4102
2 | PDCIO | PAI 1 | Input 3 | Object connected to physical input 3 | Float [SI] |  |  |  |  | 10.0 | 4103 | Float [SI] |  |  |  |  | 10.0 |  | 4103 | 4103
3 | PDCIO | PAI 1 | Input 4 | Object connected to physical input 4 | Float [SI] |  |  |  |  | 10.0 | 4104 | Float [SI] |  |  |  |  | 10.0 |  | 4104 | 4104
4 | PDCIO | PAI 1 | Input 5 | Object connected to physical input 5 | Float [SI] |  |  |  |  | 10.0 | 4105 | Float [SI] |  |  |  |  | 10.0 |  | 4105 | 4105
5 | PDCIO | PAI 1 | Input 6 | Object connected to physical input 6 | Float [SI] |  |  |  |  | 10.0 | 4106 | Float [SI] |  |  |  |  | 10.0 |  | 4106 | 4106
6 | PDCIO | PAI 1 | Input 7 | Object connected to physical input 7 | Float [SI] |  |  |  |  | 10.0 | 4107 | Float [SI] |  |  |  |  | 10.0 |  | 4107 | 4107
7 | PDCIO | PAI 1 | Input 8 | Object connected to physical input 8 | Float [SI] |  |  |  |  | 10.0 | 4108 | Float [SI] |  |  |  |  | 10.0 |  | 4108 | 4108
8
9 | PDCIO | PAI 2 | Input 1 | Object connected to physical input 1 | Float [SI] |  |  |  |  | 10.0 | 4201 | Float [SI] |  |  |  |  | 10.0 |  | 4201 | 4201
10 | PDCIO | PAI 2 | Input 2 | Object connected to physical input 2 | Float [SI] |  |  |  |  | 10.0 | 4202 | Float [SI] |  |  |  |  | 10.0 |  | 4202 | 4202
11 | PDCIO | PAI 2 | Input 3 | Object connected to physical input 3 | Float [SI] |  |  |  |  | 10.0 | 4203 | Float [SI] |  |  |  |  | 10.0 |  | 4203 | 4203
12 | PDCIO | PAI 2 | Input 4 | Object connected to physical input 4 | Float [SI] |  |  |  |  | 10.0 | 4204 | Float [SI] |  |  |  |  | 10.0 |  | 4204 | 4204
13 | PDCIO | PAI 2 | Input 5 | Object connected to physical input 5 | Float [SI] |  |  |  |  | 10.0 | 4205 | Float [SI] |  |  |  |  | 10.0 |  | 4205 | 4205
14 | PDCIO | PAI 2 | Input 6 | Object connected to physical input 6 | Float [SI] |  |  |  |  | 10.0 | 4206 | Float [SI] |  |  |  |  | 10.0 |  | 4206 | 4206
15 | PDCIO | PAI 2 | Input 7 | Object connected to physical input 7 | Float [SI] |  |  |  |  | 10.0 | 4207 | Float [SI] |  |  |  |  | 10.0 |  | 4207 | 4207
16 | PDCIO | PAI 2 | Input 8 | Object connected to physical input 8 | Float [SI] |  |  |  |  | 10.0 | 4208 | Float [SI] |  |  |  |  | 10.0 |  | 4208 | 4208
17
18 | PDCIO | PAI 3 | Input 1 | Object connected to physical input 1 | Float [SI] |  |  |  |  | 10.0 | 4301 | Float [SI] |  |  |  |  | 10.0 |  | 4301 | 4301
19 | PDCIO | PAI 3 | Input 2 | Object connected to physical input 2 | Float [SI] |  |  |  |  | 10.0 | 4302 | Float [SI] |  |  |  |  | 10.0 |  | 4302 | 4302
20 | PDCIO | PAI 3 | Input 3 | Object connected to physical input 3 | Float [SI] |  |  |  |  | 10.0 | 4303 | Float [SI] |  |  |  |  | 10.0 |  | 4303 | 4303
21 | PDCIO | PAI 3 | Input 4 | Object connected to physical input 4 | Float [SI] |  |  |  |  | 10.0 | 4304 | Float [SI] |  |  |  |  | 10.0 |  | 4304 | 4304
22 | PDCIO | PAI 3 | Input 5 | Object connected to physical input 5 | Float [SI] |  |  |  |  | 10.0 | 4305 | Float [SI] |  |  |  |  | 10.0 |  | 4305 | 4305
23 | PDCIO | PAI 3 | Input 6 | Object connected to physical input 6 | Float [SI] |  |  |  |  | 10.0 | 4306 | Float [SI] |  |  |  |  | 10.0 |  | 4306 | 4306
24 | PDCIO | PAI 3 | Input 7 | Object connected to physical input 7 | Float [SI] |  |  |  |  | 10.0 | 4307 | Float [SI] |  |  |  |  | 10.0 |  | 4307 | 4307
25 | PDCIO | PAI 3 | Input 8 | Object connected to physical input 8 | Float [SI] |  |  |  |  | 10.0 | 4308 | Float [SI] |  |  |  |  | 10.0 |  | 4308 | 4308
26
27
28 | * These objects are not available when option Battery Supervision is enabled.
29
30 | Gäller fr o m IPC firmware version 1-1.0.2
31

## Data
Analog types | Slave | Master | Port settings | Baud rate | Indication | Command
Normalized [0-100%] | No slave | No master | 2-wire (RS-485) | 1200 | SP | SC
Normalized [0-120%] | -101 slave | -101 master | 4-wire (RS-422) | 2400 | DP | DC
Float [SI] | -104 slave |  | RS-232 without flow control | 4800
Scaled [SI*1] |  |  | RS-232 with flow control | 9600
Scaled [SI*10]
Scaled [SI*100]